## Slide 1: Mitchell Lee Micro-grid vs Solar Home Systems Progress Reports
November 7, 2013

## Slide 2: HOMER Models
Modeled current system using ug01 demand (sum of circuits, ignoring metering losses).
Optimally sized SharedSolar system for ug01 demand (sum of circuits, ignoring metering losses) for a range of reliabilities.
Optimally Sized home systems using historical data for:
  a “big” consumer
  “small” consumer who briefly had elevated levels of energy consumption
  “small” consumer

## Slide 3: INPUT DATA

## Slide 4
Input Data

## Slide 6
Input Data: Sample “Big” Customer

## Slide 8
Sample “Small” Customer
Short period with TV

## Slide 12: Cost Assumptions
PV – 1 USD/W, design life20 years.
Battery – 0.52 USD/Wh capacity, min SOC = 40 %, battery life depend on use.
Inverter – 0.60 USD/W capacity, 15 year design life
Project life of 25 years

## Slide 13: HOMER MODEL RESULTS

## Slide 14: Model of Current System
PV (kW) | Battery (kWh) | Converter (kW) | Initial capital | Operating cost ($/yr) | Total NPC | COE ($/kWh) | Capacity shortage
1.4 | 17.28 | 0.75 | $5,090 | 543 | $12,027 | 2.649 | 0
Battery lifespan is 5 years in simulation
This model uses size of currents system, and current consumer demand. Metering losses are not included in consumption making the system seem even more oversized.

## Slide 15: Current System Optimally Sized
Max. Cap. Shortage (%) | PV (kW) | # of Batteries CP12240D | Battery (kWh) | Converter (kW) | Initial capital | Operating cost ($/yr) | Total NPC | COE ($/kWh) | Capacity shortage
0 | 0.8 | 16 | 4.608 | 0.8 | $2,144 | 163 | $4,233 | 0.933 | 0
0.5 | 0.8 | 16 | 4.608 | 0.6 | $2,024 | 160 | $4,070 | 0.897 | 0
1 | 0.6 | 16 | 4.608 | 0.6 | $1,824 | 159 | $3,854 | 0.855 | 0.01
1.5 | 0.6 | 16 | 4.608 | 0.6 | $1,824 | 159 | $3,854 | 0.855 | 0.01
2 | 0.6 | 16 | 4.608 | 0.4 | $1,704 | 155 | $3,680 | 0.82 | 0.02
5 | 0.6 | 12 | 3.456 | 0.4 | $1,488 | 161 | $3,552 | 0.802 | 0.03
10 | 0.4 | 12 | 3.456 | 0.4 | $1,288 | 149 | $3,196 | 0.768 | 0.1
Battery lifespan is between 3 and 5 years in simulations

## Slide 16: UG01-5: Solar Home System
Max. Cap. Shortage (%) | PV (kW) | CP12240D | Battery Capacity (kWh) | Converter (kW) | Initial capital | Operating cost ($/yr) | Total NPC | COE ($/kWh) | Capacity shortage
0 | 0.28 | 8 | 2.304 | 0.2 | $800 | 70 | $1,693 | 1.381 | 0
0.5 | 0.28 | 6 | 1.728 | 0.2 | $700 | 54 | $1,390 | 1.137 | 0
1 | 0.3 | 5 | 1.44 | 0.2 | $670 | 47 | $1,266 | 1.039 | 0.01
1.5 | 0.26 | 5 | 1.44 | 0.2 | $630 | 46 | $1,220 | 1.007 | 0.01
2 | 0.24 | 5 | 1.44 | 0.2 | $610 | 46 | $1,197 | 0.991 | 0.02
5 | 0.18 | 5 | 1.44 | 0.2 | $550 | 45 | $1,124 | 0.949 | 0.04
10 | 0.16 | 4 | 1.152 | 0.2 | $480 | 45 | $1,053 | 0.925 | 0.08

## Slide 17: UG01-1: Solar Home System
Max. Cap. Shortage (%) | PV (kW) | CP12240D | Battery Capacity (kWh) | Converter (kW) | Initial capital | Operating cost ($/yr) | Total NPC | COE ($/kWh) | Capacity shortage
0 | 0.08 | 3 | 0.864 | 0.1 | $290 | 26 | $627 | 3.3 | 0
0.5 | 0.06 | 3 | 0.864 | 0.1 | $270 | 26 | $604 | 3.182 | 0
1 | 0.12 | 2 | 0.576 | 0.1 | $280 | 19 | $520 | 2.765 | 0.01
1.5 | 0.08 | 2 | 0.576 | 0.1 | $240 | 18 | $475 | 2.527 | 0.01
2 | 0.06 | 2 | 0.576 | 0.1 | $220 | 18 | $452 | 2.413 | 0.02
5 | 0.06 | 2 | 0.576 | 0.1 | $220 | 18 | $452 | 2.413 | 0.02
10 | 0.06 | 1 | 0.288 | 0.1 | $170 | 10 | $300 | 1.704 | 0.08

## Slide 18: UG01-2: Solar Home System
Max. Cap. Shortage (%) | PV (kW) | CP12240D | Battery Capacity (kWh) | Converter (kW) | Initial capital | Operating cost ($/yr) | Total NPC | COE ($/kWh) | Capacity shortage
0 | 0.04 | 1 | 0.288 | 0.1 | $150 | 10 | $278 | 1.582 | 0
0.5 | 0.02 | 1 | 0.288 | 0.1 | $130 | 10 | $255 | 1.456 | 0
1 | 0.02 | 1 | 0.288 | 0.1 | $130 | 10 | $255 | 1.456 | 0
1.5 | 0.02 | 1 | 0.288 | 0.1 | $130 | 10 | $255 | 1.456 | 0
2 | 0.02 | 1 | 0.288 | 0.1 | $130 | 10 | $255 | 1.456 | 0
5 | 0.02 | 1 | 0.288 | 0.1 | $130 | 10 | $255 | 1.456 | 0
10 | 0.02 | 1 | 0.288 | 0.1 | $130 | 10 | $255 | 1.456 | 0

## Slide 19: Cost per Unit Energy Comparison
 | COE ($/kWh) |  |  | 
Max. Cap. Shortage (%) | UG01-All | UG01-5 | UG01-1 | UG01-2
0 | 0.933 | 1.381 | 3.3 | 1.582
0.5 | 0.897 | 1.137 | 3.182 | 1.456
1 | 0.855 | 1.039 | 2.765 | 1.456
1.5 | 0.855 | 1.007 | 2.527 | 1.456
2 | 0.82 | 0.991 | 2.413 | 1.456
5 | 0.802 | 0.949 | 2.413 | 1.456
10 | 0.768 | 0.925 | 1.704 | 1.456
  UG01-5: a “big” consumer
  UG01-1: “small” consumer who briefly had elevated levels of energy consumption
  UG01-2: “small” consumer